## Slide 1
Building Wind Farms Next to Series Capacitor Banks: Lessons Learned
Ahmad Abdullah, Billy Yancey and Mahdi Kefayati

## Slide 2
TITLE
OUTLINE
A subsynchrnous oscillations study for a wind project in ERCOT
The project is located next to large series capacitor banks that compensate 100% of line length
A fault nearby would cause the project to go offline
Investigations showed that the trip is not due to SSO but due to the proximity to series capacitor banks

## Slide 3
TITLE
TITLE
A frequency scan analysis
A detailed electromagnetic transient (EMT) study
Investigations of the trip of wind farm
COMPANY PROFILE
TITLE
Contents

## Slide 4
TITLE
TITLE
SSO has become a concern to ISOs and TSOs since the two incidents of shaft damage experienced at the Mohave generating station
The subject has received renewed attention due to the incident that occurred in Texas in 2009 which revealed that inverter based generation can also be affected by SSO
ERCOT requires an SSO study before project energization
COMPANY PROFILE
TITLE
Introduction

## Slide 5
TITLE
TITLE
Done for screening purposes
The purpose of the scan is to reduce the number of cases needed for detailed EMT analysis
A grid side scan and a project side scan under different operating conditions are done
Both the grid side and the project side scans are combined to assess the amount of damping resistance available when the reactance crosses zero
COMPANY PROFILE
TITLE
Frequency Scan Analysis

## Slide 6
TITLE
TITLE
  Performed to determine the contingencies, up to N-5, that result in the WP to become near radial or radially connected to the series compensated transmission lines
  Used to calculate the equivalent resistance and reactance looking into the transmission network at the project’s POI for different contingency conditions, up to N-5, that may show vulnerability to SSO due to becoming radially connected to series compensation capacitors
  Additionally, for each of these contingencies, various combinations of sensitivities were evaluated. These sensitivities are:
    The switched shunts are switched ON or OFF
    The series capacitor banks are ON or OFF
    Various generation levels and wind output in the Panhandle area
COMPANY PROFILE
TITLE
Grid side scan

## Slide 7
TITLE
TITLE
A total of 350 scans have been performed
COMPANY PROFILE
TITLE
Grid side scan
Frequency scan with no contingency
Frequency scan under different contingency conditions

## Slide 8
TITLE
TITLE
  This frequency scan looked into the WP from the POI and included the wind turbines, the most recent collection system design and layout as well as the current main power transformer and pad mount transformers
  The results from the project frequency scan show that the reactance of the project is positive for all frequencies under study
  Various sensitivities were evaluated. These sensitivities are:
    The series compensation option turned ON or OFF
    The wind generation of the project
COMPANY PROFILE
TITLE
Project side frequency scan

## Slide 9
TITLE
TITLE
COMPANY PROFILE
TITLE
Project side frequency scan
10% output with series compensation OFF
10% output with series compensation ON

## Slide 10
TITLE
TITLE
COMPANY PROFILE
TITLE
Project side frequency scan
100% output with series compensation OFF
100% output with series compensation ON

## Slide 11
TITLE
TITLE
COMPANY PROFILE
TITLE
Combined Frequency Scan
10% output
100% output

## Slide 12
TITLE
TITLE
COMPANY PROFILE
TITLE
Detailed EMT Analysis
Three phase fault on transmission line A-B
Fault is cleared within 5 cycles
Monitored at POI:
  Active and reactive power
  Voltage and frequency
The objective is to observe whether the project remains stable after fault clearing

## Slide 13
TITLE
TITLE
Turbines will trip after fault clearing
Turbines absorbing enormous reactive power
COMPANY PROFILE
TITLE
Detailed EMT analysis - Results
Reactive Power
POI Voltage

## Slide 14
TITLE
TITLE
COMPANY PROFILE
TITLE
Explanation of trip event
Series Capacitor bank is compensating 100% of line length
The bank stays online during and after clearing the fault (design decision by TSO)
During fault, capacitor charges
After fault, the voltage changes abruptly causing enormous reactive power to be release to the project

## Slide 15
TITLE
TITLE
Short Circuit series capacitor bank during fault (rejected by TSO due to technical reasons)
Obtain a waiver for the project to trip during fault (granted by ERCOT)
COMPANY PROFILE
TITLE
Recommendations

## Slide 16
TITLE
TITLE
Questions?
Thanks you!
COMPANY PROFILE
TITLE